This SWMS must be reviewed with all workers before works commence. Work must stop immediately if controls cannot be maintained or conditions change.

| ACTIVITY / TASK: | Excavations in a Live Substation or Around Live Underground Services | LOCATION: | MILC - Millchester Substation / Project Specific |
| --- | --- | --- | --- |
| SCOPE: | Applies to all Austen Landscaping & Earthmoving workers undertaking trenching and/or excavation in live substations or around live underground services. | SWMS NO: | MLCH-05 |
| TRAINING & EXPERIENCE: | Licensed and competent operators, experienced workers, site inducted personnel and ESO where required. | PREPARED BY: | John Austen |
| SITE RISK ASSESSMENT BY: | Site Supervisor: John Austen | CREATION / REVIEW DATE: | 15/05/2026 |

| RISK ASSESSMENT (HAZARD IDENTIFICATION) |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Gravity Objects falling ☒ |  | Hazard Substances Skin contact ☒ |  |  |  | Radiation Ultra Violet |  |  | ☒ | EMP | ☐ |
| People falling ☒ |  | Inhalation ☐ |  |  |  | Arc flashes |  |  | ☒ | Soil erosion | ☒ |
| Lifting ☒ |  | Ingestion ☐ |  |  |  | Microwaves |  |  | ☐ | Spills to drains/waterways | ☐ |
| Carrying ☒ |  | Extremes of Hot surface contact ☒ |  |  |  | Lasers |  |  | ☐ | Spills to ground | ☒ |
| Kinetic Projectiles ☒ |  | Temperature Cold surface contact ☐ |  |  |  | Electrical Electrocution |  |  | ☒ | Air pollution (dust, fumes) | ☒ |
| Penetrating objects ☐ |  | Heat stress ☐ |  |  |  | Burns |  |  | ☒ | Flora/Fauna impact | ☒ |
| Mechanical Caught between ☒ |  | Heat illness ☒ |  |  |  | Shocks |  |  | ☒ |  |  |
| Struck by ☒ |  | Frostbite ☐ |  |  |  | Glare |  |  | ☐ | Other |  |
| Struck against ☒ |  | Hypothermia ☐ |  |  |  | Vibration Circulation |  |  | ☐ | Static Plant | ☐ |
| Sound Hearing damage ☒ |  | Biological Inhalation ☐ |  |  |  | Back |  |  | ☒ |  |  |
| Thermal Hot matter spills ☐ |  | Irritation ☐ |  |  |  | Hand |  |  | ☒ | Mobile Plant | ☒ |
| Hot matter splashes ☐ |  | Absorptive (cuts) ☐ |  |  |  | Noise Plant |  |  | ☒ |  |  |
| Muscular Twisting or reaching ☒ |  | Skin pores ☐ |  |  |  |  |  |  |  | Safety Equipment | ☐ |
| Lifting or pushing ☒ |  | Ingestion ☐ |  |  |  |  |  |  |  |  |  |
| RISK ASSESSMENT (POTENTIAL OUTCOMES) |  |  | MINOR TO SEVERE |  |  |  |  |  |  | PRECAUTIONS & PERMITS |  |
|  |  |  | INSIGNIFICANT | MINOR | MODERATE |  | MEDIUM | MAJOR | EXTREME | Hot Work Confined Space Hazard work clearance High Voltage Access Excavation Scaffolding Lock Out/Tag Out Fall Arrest Lighting Erect warning signage | ☐ ☐ ☐ ☒ ☒ ☐ ☐ ☐ ☐ ☐ |
| Strain / overuse injuries and diseases to back, shoulder, wrist, elbow, knee, ankle |  |  | ☐ | ☐ | ☒ |  | ☐ | ☐ | ☐ |  |  |
| Cuts and abrasion injuries to eyes, hands, fingers, feet and head |  |  | ☐ | ☐ | ☒ |  | ☐ | ☐ | ☐ |  |  |
| Impact and crush injuries to the head, feet and fingers (falls, caught between) |  |  | ☐ | ☐ | ☐ |  | ☐ | ☒ | ☐ |  |  |
| Burns (by heat, power, light (UV) or chemicals) to the eyes, feet and skin |  |  | ☐ | ☐ | ☐ |  | ☐ | ☒ | ☐ |  |  |
| Noise induced hearing loss |  |  | ☐ | ☐ | ☒ |  | ☐ | ☐ | ☐ |  |  |
| Toxic effects to respiratory system or skin |  |  | ☐ | ☒ | ☐ |  | ☐ | ☐ | ☐ |  |  |
| CONTROL MEASURES |  |  |  |  |  |  |  |  |  |  |  |
| Short Term (e.g. training) | Competent workers (certificated), Pre-start meeting; Experienced in manual handling, use of PPE; Follow SWMS |  |  |  |  |  |  |  |  |  |  |
| Long Term (e.g. redesign) | Not determined |  |  |  |  |  |  |  |  |  |  |

| ACTIVITIES INVOLVING HIGH RISK WORK |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Demolition of load bearing structure |  |  | ☐ |  | Near pressurised gas distribution mains |  |  |  | ☐ | Near electrical installations/services |  |  |  | ☒ |
| Risk of falling >2m |  |  | ☐ |  | Asbestos work |  |  |  | ☐ | Confined space |  |  |  | ☐ |
| Near powered mobile plant |  |  | ☒ |  | Work on Towers |  |  |  | ☐ | Excavations or shafts >1.5m deep |  |  |  | ☒ |
| Structural alterations requiring temporary support |  |  | ☐ |  | On or near water where there is a risk of drowning |  |  |  | ☐ | Work on or next to roads/railways |  |  |  | ☐ |
| Contaminated / flammable areas |  |  | ☐ |  | Tilt up / pre cast work |  |  |  | ☐ | Involving explosives |  |  |  | ☐ |
| RISK ASSESSMENT (DETERMINATION OF APPROPRIATE EQUIPMENT TO USE) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Eye Protection | Safety Helmet | Hearing Protection |  | Half Face Respirator |  | Disposable Respirator | Safety Footwear | Hand Protection |  |  | UV Protection | Protective Clothing | Other |  |
| Yes- Medium Impact | Yes | As per Risk Assessment |  | N/A |  | N/A | Yes | Task specific. 1000v Insulated Gloves |  |  | 30+ Sunscreen | 100% Cotton Clothing (Hi Vis) |  |  |

Step 1 - Assess the most expected consequence of an event

| CONSEQUENCE | SAFETY | ENVIRONMENTAL | QUALITY |
| --- | --- | --- | --- |
| CATASTROPHIC | - Single or multiple Fatality - Regulatory Prosecution/Enforcement order | - Irreversible and/or offsite damage, - Clean up or remedy from damage result is remediation will require emergency services, work lasting >12 months, - Regulatory notification compulsory with public investigation likely, - Impact on local community leads to community outrage | - Rework costs > $50k, - Loss of accreditation |
| MAJOR | - Permanent disabling injury or occupational illness - Lost time injury or occupational illness lasting > 3 days - Regulatory Infringement Notice / Prohibition Notice | - Long term on/offsite environmental damage, pollution or degradation, - Clean up, remediation or rehabilitation will require external specialist >1 week <1 months - Impact on local community leads to community outrage | - Rework costs >$20k <$50k, - Critical Audit Finding (NCR) - Accreditation warning, Client sanctions, Contract penalties. |
| MODERATE | - Lost time injury or occupational illness lasting ≤ 3 days - Regulatory Improvement Notice / Written Warning | - Medium term onsite environmental damage; - Clean up, remediation or rehabilitation works will require >1 day <7 days | - Rework costs >$10k <$20k, - Major Audit Finding (NCR) - Client dissatisfaction, - Delays to project program. |
| MINOR | - Offsite medical treatment - Regulatory Verbal Warning | - Short term onsite environmental damage, - Limited onsite impacts clean up, remediation or rehabilitation works will require up to <24 hours | - Rework costs >$5k <$10k. - Minor Audit Finding (NCR) |
| INSIGNIFICANT | ▪ Onsite first aid treatment ▪ No Regulatory Involvement | - Minor onsite environmental damage, - Minor clean up, remediation or rehabilitation works will require <8 hours | - Rework costs <$5k. - Minor defect accepted as is or audit recommendation |

HIGH RISK WORK INTERFACE

Moving powered plant may interact with high risk construction work, including work near electrical installations/services, excavation work, live substations, traffic interfaces and work near underground services. Where these conditions apply, the relevant task-specific SWMS must also be reviewed and followed.

RISK RATING GUIDE

| Risk Rating | Required Action |
| --- | --- |
| Extreme | Do not proceed. Alternative method required. |
| High | Senior management / supervisor approval required before work proceeds. |
| Medium | Management responsibility must be specified and controls monitored. |
| Low | Work may proceed with normal supervision and routine controls. |
| Stop Work | All workers have authority to stop work if controls cannot be maintained. |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk |  | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- | --- |
| Planning, preparation, verification of competency. | Legislation Breach | 1 | ▪ ▪ ▪ ▪ ▪ ▪ ▪ ▪ | All workers to have general industry induction card (Blue/White Card) and to be site inducted All workers will be inducted in and sign off on all SWMS relevant to their works - Induction to cover safe work practices and access in a live substation. Supervisor to sight & record relevant qualifications & competencies Plant registered as required All plant logs current & maintained Maintenance on all plant & equipment is done in accordance with legislative requirements & manufacturer’s instructions & specifications. All electrical tools, leads & equipment have current test & tag and are in good order and condition. Workers shall be dressed in site PPE requirements and use task specific PPE as required | 4 | Supervisor |
|  | Use of untrained or incompetent workers | 1 | ▪ ▪ ▪ ▪ ▪ ▪ ▪ ▪ ▪ | All workers shall have read, understood and signed onto the relevant SWMS for the works All workers to attend Austen Prestart meeting daily before commencing work All workers are trained and competent in their relevant task and hold relevant licenses/certification Supervisor to ensure all workers understand the sequence of work At Pre start, if any additional hazards are identified, consultation between Supervisor and site workers will assess risks and put in additional control measures to complement SWMS as required Supervisor to regularly observe and monitor workers & inspect tasks Workers to attend all scheduled Toolbox talks when on site Supervisor to maintain appropriate communication systems and signals should be understood by all (i.e. positive communication signals between plant operators and workers and between workers carrying out tasks in conjunction with one another). Role of ESO to be fully explained to all workers involved in working near live electrical parts | 4 | Supervisor / All Workers |
|  | Faulty plant or equipment | 2 | ▪ ▪ ▪ ▪ ▪ | Maintenance done in accordance with manufacturer’s instructions and guidelines Plant Operator’s to complete inspection & fill in pre start inspection record prior to using daily. Workers to check all plant, equipment, electrical and hand tools before use Check all communication devices are operating and fully charged Faults, malfunctions and damage to be reported immediately | 4 | Supervisor / Operator |
|  | Uncontrolled and unauthorised access and egress by persons and / or mobile plant | 1 | ▪ ▪ ▪ | Erect barricading and signage as required and where necessary Monitor work area for unauthorised persons External parties allowed access should read through and understand the work process and sign off that they understand before being allowed entry to controlled areas. | 4 | Supervisor / All Workers |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Planning and preparation for Excavation in Live Substation | Electric shock from striking buried electrical cables | 1 | ▪ Prior to commencing any excavation or trenching work, over 200mm in-depth the Site Supervisor shall prepare or obtained from PC an Excavation Permit with the following records/information: - A detailed drawing of the extent of the excavation work shall be reviewed; - A DBYD (Dial before you dig report) shall be obtained for the excavation site and reviewed for the existence/location of existing services; - Any available existing drawings of the existing infrastructure shall be reviewed for the existence/location of existing services; - Consult with relevant parties (Client/Authority) who have experience with the excavation site; - Workers are to walk the area of the proposed excavation, inspecting existing pits, cable trenches and foundations for presents of conduits or cables. - Cable locating equipment shall be used by a Competent Person to sweep the excavation site to locate any possible unknown services and to position any known services. - All services identified with the cable locating equipment shall be marked on the ground with orange paint or similar and their location marked up on a site layout plan (with measurements) and photos taken for recovery purposes should the marks be lost. - Once services have been identified with the cable locating equipment, those services located within 1000mm of the edge of excavation shall be pot holed to confirm their exact location prior to any mechanical excavation. - Ergon approved ESO is to supervisor all excavations within 1000mm of a live U/G service. - Before installing pegs over a depth of 200mm from the existing platform level, Workers shall review the Excavation permit for the presents of U/G services. | 4 | Supervisor / All Workers |
| Pot Holing by Hand | Electric shock from striking buried electrical cables while excavating | 1 | - All excavations within 1000mm of where live cables are identified or suspected of being present shall be completed under the supervision of an ESO, who should maintain appropriate communication lines/systems with the workers involved in the task, who must comply with any direction given - Any areas where live cables are identified or suspected of being present shall be excavated by hand using 1000v insulated gloves and fibreglass or nonconductive shovels and insulated tools. - Hand excavation should expressly avoid using crowbars or jackhammers unless the ground surface is too hard to break with a fibreglass shovel, in which case these tools should only be used until the ground surface gives way to softer ground. Workers must continue digging with nonconductive shovel. | 4 | Supervisor / ESO All Workers |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Pot Holing by Hand (cont’d) | Electric shock from striking buried electrical cables while excavating (cont’d) | 1 | - If a crowbar is to be used, it shall be insulated and the user must wear 1000v insulated gloves - If a jackhammer is to be used it should be fitted with a spade bit and the user must wear 1000v insulated gloves - If direct buried cables are suspected to be underground with no clear indication of position or depth, then vacuum excavation may be required | 4 | Supervisor / ESO All Workers |
|  | Electric shock due to faulty insulated glove | 1 | - Insulating gloves are to be tested at intervals not more than six months - Immediately prior to use, insulating gloves are to be visually examined for any sign of damage or deterioration. Users are to stretch the gloves by hand to ensure the mechanical strength is adequate and then test the glove by rolling it from the cuff to force air into it. Workers must roll gloves to detect if airtight before use - Any defective or out of date insulated gloves must be discarded or tagged out of service - If the insulated glove or outer glove is damaged at any time during the works it shall be immediately replaced - Insulating gloves to be stored unfolded, in a cool, dry place, away from direct sunlight between use. | 4 | Supervisor / All Workers |
|  | Electric shock due to incorrectly worn insulated gloves | 1 | ▪ There are four layers to a correctly worn insulating glove, - The inner glove, which protects the insulating glove from the inside, - The powder, which protects the insulating glove from friction on the inside, c) The insulating glove, and d) The outer glove, which protects the insulating glove from external mechanical damage ▪ To wear a set of insulating gloves correctly the user shall place the inner glove over clean and dry hands, sufficient powder is to be placed into each insulating glove prior to placing the insulating gloves over the inner gloves, which is followed by the outer gloves | 4 | Supervisor / All Workers |
|  | Electric shock from contacting or entering safe approach distance of a live exposed part | 1 | - Crow bars should only be used in areas clear of overhead exposed parts - Shovels shall not be taken above the worker’s shoulders | 4 | Supervisor / All Workers |
|  | Muscular Injury | 2 | - Workers are to be fit for work and stretch before commencing task - Workers shall be rotated from task or given rest breaks as necessary - Workers shall use correct manual handling technique when completing manual tasks - Workers shall use long handle shovels and equipment to avoid the need to bend excessively | 4 | All Workers |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Pot Holing by Vacuum Excavation | Electric shock from striking buried electrical cables while excavating | 1 | - All excavations within 1000mm of where live cables are identified or suspected of being present shall be completed under the supervision of an ESO, who should maintain appropriate communication lines/systems with the workers involved in the task, who must comply with any direction given by ESO. - In any areas where live cables are identified or suspected of being present, the operator of the pressure hose and suction hose shall wear 1000v insulated gloves - The pressure of the hydro vacuum excavator shall be set at 2000psi | 4 | Supervisor / ESO Operator |
|  | Electric shock from contacting or entering safe approach distance of a live exposed part | 1 | - Water jet shall always be directed towards the ground - The trigger of the pressure hose shall never be bypassed - All works within the nominated exclusion zone of the exposed live part shall be completed under the supervision of an ESO. | 4 | Supervisor / Operator |
|  | Contaminated Soils (Asbestos, PCB’s Acid Sulphate, etc.) | 2 | - Hydro vacuum excavation shall not be utilised where the ground is suspected of being contaminated with asbestos, PCB’s Acid Sulphate Soils, etc. - Where it is not practical not to use hydro vacuum excavation, then where possible, the waste generated shall be disposed of onsite, in soil bunds constructed in the affected area of the site, or the material must be taken to an approved disposal site. - Refer to the SWMS for Hydro Vacuum Excavation for the safe operation of the Hydro Vacuum Unit. | 4 | Supervisor / Operator |
| Mechanical excavation in or around a live substation | Electric shock from striking buried electrical cables while excavating | 1 | - A spotter shall be used at all times while excavations take place, should the spotter notice something that suggests an un-identified cable or conduit containing a cable exists (such as signs of a trench, marker tape, bedding sand, etc) then the spotter shall stop the machine operator, and the area shall be potholed to verify whether or not an un-identified cable or conduit containing a cable exists. The area shall be pot holed to the depth and width of the required excavation and until such time the crew is confident no services are present - The spotter shall maintain appropriate communication lines/systems with the operator involved at all times. | 4 | Supervisor / ESO Operators / Spotter |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk |  | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- | --- |
| Mechanical excavation around an in-service (LIVE) HV direct buried electrical cables | Electric shock from striking buried electrical cables while excavating | 1 | ▪ ▪ ▪ ▪ | No mechanical excavation shall take place until all identified cables within 1000mm of the excavation site have been positively located via pot holing No mechanical excavation shall take place within 1000mm of a live direct buried cable without the supervision of an ESO, who should maintain appropriate communication lines/systems with the workers involved in the task, who should comply with any direction given. No mechanical excavation is to take place within: - 500mm of either side of a direct buried cable - 500mm above a direct buried cable, unless the direct buried cable has been positively identified as having mechanical protection (such as hard cable cover) installed 300mm above the cable. In this case, mechanical excavation must stop at the mechanical protection - At no stage is mechanical excavation permitted below a direct buried cable All excavations within these distances shall be completed by manual excavation or vacuum excavation. | 4 | Supervisor / ESO Operators / Spotter |
| Mechanical excavation around an in-service (LIVE) HV electrical cable contained within a conduit | Electric shock from striking buried electrical cables while excavating | 1 | ▪ ▪ ▪ a) b) c) ▪ | No mechanical excavation shall take place until all identified cables within 1000mm of the excavation site have been positively located via pot holing No mechanical excavation shall take place within 1000mm of a live cable contained within a conduit without the supervision of an ESO, who should maintain appropriate communication lines/systems with the workers involved in the task, who should comply with any direction given No mechanical excavation is to take place within: 300mm of either side of a cable contained in a conduit 300mm above a cable contained in a conduit, At no stage is mechanical excavation permitted below a cable contained in a conduit All excavations within these distances shall be completed by manual excavation or vacuum excavation | 4 | Supervisor / ESO Operators / Spotter |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Mechanical excavation around an in-service (LIVE) LV electrical cable direct buried or contained within a conduit | Electric shock from striking buried electrical cables while excavating | 1 | - No mechanical excavation shall take place until all identified cables within 1000mm of the excavation site have been positively located via pot holing - No mechanical excavation shall take place within 1000mm of a live cable contained within a conduit without the supervision of an ESO, who should maintain appropriate communication lines/systems with the workers involved in the task, who should comply with any direction given - No mechanical excavation is to take place until the conduit has been fully exposed by manual or vacuum excavation - No mechanical excavation is to take place around an exposed direct buried cable until mechanical protection has been installed around/beside the exposed direct buried cable - No mechanical excavation shall take place under any exposed cable or conduit containing a cable | 4 | Supervisor / ESO Operators / Spotter |
| Mechanical excavation around an out of service (DEAD) electrical cable | Damage to infrastructure that could cause electric stock when decommissioned | 1 | - All out of service cables shall be treated as important as a live cable. Once re-commissioned they will be live and any damage may have potential to cause significant injury and death - The appropriate authority shall be advised of any damage to out of service cables - No mechanical excavation shall take place until all identified cables within 1000mm of the excavation site have been positively located via pot holing - No mechanical excavation is to take place until the conduit has been fully exposed by manual or vacuum excavation - No mechanical excavation is to take place around an exposed direct buried cable until mechanical protection has been installed around/beside the exposed direct buried cable - No mechanical excavation shall take place under any exposed cable or conduit containing a cable | 4 | Supervisor / Operators / Spotter |
| Mechanical excavation around comms, fibre optic or signaling cable direct buried or contained within a conduit | Damage to vital equipment (includes danger of damaging fail-safe service). | 1 | - No mechanical excavation shall take place until all identified cables within 1000mm of the excavation site have been positively located via pot holing - No mechanical excavation is to take place until the conduit has been fully exposed by manual or vacuum excavation - No mechanical excavation is to take place around an exposed direct buried cable until mechanical protection has been installed around/beside the exposed direct buried cable - No mechanical excavation shall take place under any exposed cable or conduit containing a cable | 4 | Supervisor / Operators / Spotter |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Mechanical excavation around Gas or other services | Risk of fire explosion or damage to equipment or services | 1 | - No mechanical excavation shall take place until all identified services within 1000mm of the excavation site have been positively located via pot holing - No mechanical excavation is to take place until the services have been fully exposed by manual or vacuum excavation and mechanical excavation is approved by an appropriate representative of the relevant utility - All excavations are to be completed in accordance with the utilities stated procedures - No mechanical excavation shall take place under any exposed gas pipe or other services | 4 | Supervisor / Operators / Spotter |
| Mechanical excavation around an earthing grid | Electric shock from breaking and rejoining earth cables1 | 1 | - Care shall be taken to ensure earthing cables are not broken or damaged during mechanical excavation - Where the location of the earthing grid is known, the earthing grid shall be marked out where it crosses with the excavation - The spotter shall locate and carefully clean any soil from around the earthing cable and expose the cable prior to mechanical excavations continuing - If the earthing grid is broken, the crew shall immediately notify the site supervisor, who shall organise for its repair as soon as possible - All earthing grid repairs are to be completed by a licensed and experienced electrician - No Austen worker is permitted to cut an existing earthing grid. If required to be cut, the earthing grid shall be cut by a licensed and experienced electrician and the earthing re-run or temporarily bridged - Note: should an excavator or similar, have hooked on to an earthing grid, investigation may be necessary to ensure the wire has not been broken further along the wire (such as at an intersection) | 4 | Supervisor / Operators / Spotter |
| Mechanical excavation around exposed live parts | Electric shock from contact with overhead electrical equipment | 1 | ▪ At any time mechanical plant is required to encroach on the safe approach distance of any live exposed part, an ESO is required to supervise if plant is to be operated within: - 3 m of an exposed live part of a voltage of less or equal to 132kv, - 6 m of an exposed live part of a voltage of greater then 132kv, or has the potential to enter the safe approach distance of an exposed live part - A Spotter is required any time mechanical plant has the potential to encroach upon the 6m exclusion zone of a live exposed part without supervision - ESO or Spotter must maintain appropriate communication lines/systems with the operator involved in the task at all times - Plant selection shall be appropriate to operate safely within vicinity of the exposed live electrical parts - Electronic limiters to restrict operating radius of excavator boom to prevent encroachment into exclusion zone may be used if required. | 4 | Supervisor / ESO/ Operators / Spotter |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Mechanical excavation around exposed live parts (cont’d) | Electric shock when high voltage electricity arcs across an air gap | 1 | ▪ Trailing earths may be required to be installed to plant to reduce the risk of induced voltages, the requirement for trailing earths will be determined by the ESO, trailing earths shall be installed and removed by the ESO | 4 | Supervisor / Operators / Spotter |
| Excavation in Live Substation (general) | Asbestos |  | - There is an increased risk that Asbestos Conduits may be present in older substations, existing drawings and the site Asbestos Register shall be reviewed to identify whether Asbestos is present. - The point where a conduit exits a slab or pit may also identify whether it’s an Asbestos conduit. - If conduits are suspected of containing asbestos, all workers directly involved in the task shall cease work until appropriate SWMS for ACM removal is developed and/or specialist, licenced contractors shall be used to remove ACM. - Excavated soil shall be kept wet and returned to the excavation as soon as possible ▪ Any exposed asbestos conduit shall be sprayed with 4 parts water to 1 part PVC glue. - Under no circumstances is the conduit to be broken, cut or removed. |  |  |
|  | Breach of Authority Procedure | 1 | ▪ Where a discrepancy exists between any measurement or control stated within this document and that of the relevant Authority then the document with the highest control measure shall be adopted | 4 | Supervisor |
|  | Hand Injury (Cuts and nicks) | 3 | ▪ Workers completing manual task shall be wearing hand protection | 4 | All Workers |
|  | Dehydration | 2 | - Workers are to ensure they maintain their hydration levels by drinking water - Workers shall have a wide brim attachment for their helmets - Workers shall be dressed in long cotton clothing | 4 | All Workers |
|  | Faulty communication | 1 | ▪ All workers are to ensure that clear and exact communications are maintained, in particular ESOs/spotters and operators are to ensure that both parties are aware of what the other party expects for example: - the operator expects a spotter or observer to advise the operator when it is not safe to continue - the spotter expects the operator to stop 500mm away from the spotters shovel which is identifying the location of a live LV/HV wire. | 4 | Supervisor / All Workers |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |
| Contact with and Repair of Electrical conduits | Electrocution | 1 | ▪ If a conduit is contacted and damaged, all care and consideration should be taken to ascertain if conduit contains live HV or LV cables. Supervisor must ensure PC is informed and if necessary relevant energy authority. Process to identify if live is to check drawings and check for nearby pits to identify if conduits line up with direction from pit. If still unclear, hand saw only to be used to carefully cut into top of conduit and 1000v insulated gloves to be worn to allow for inspection of inside of conduit. Under no circumstances are power tools to be used to cut through conduits until they are clearly identified as free of live HV or LV. | 4 | Supervisor /All Workers |
| Contact with and Repair of Comms conduits | Damage to service inside comms conduit | 2 | ▪ If a conduit is contacted and damaged, all care and consideration should be taken to ascertain if conduit contains live comms or fire optic cables. Supervisor must ensure PC is informed and if necessary relevant energy authority. Process to identify if live is to check drawings and check for nearby pits to identify if conduits line up with direction from pit. If still unclear, hand saw only to be used to carefully cut into top of conduit to allow for inspection of inside of conduit. Under no circumstances are power tools to be used to cut through conduits until they are clearly identified as free of comms or fibre optic cables. | 4 | Supervisor /All Workers |
| Task Observation and Monitoring Task Observation and Monitoring (cont’d) | Unforeseen or previously unidentified hazards | 2 | - Supervisors to monitor and observe tasks and work activities - Supervisor to conduct regular field inspections - Review of site inspections and supervisor observations shall be carried out by Project Manager - All workers to monitor for additional hazards. If an additional hazard is identified, immediately stop work and remove hazard if possible, report the observation to supervisor, conduct risk assessment and supervisor to review and change SWMS accordingly. Do not start work until hazard is controlled | 4 | Supervisor / All Workers |
|  | Unforeseen changes to work procedures or conditions | 2 | - Any additional works in area shall be communicated at morning prestart. - Perform task risk assessment at the beginning of each day - Review relevant SWMS each week or as conditions change - Supervisor to monitor weather conditions throughout the day and cease works if weather conditions become unsafe | 4 | Supervisor / All Workers |

| SEQUENCE OF WORK Sequence of each type of work | RISK ASSESSMENT List anticipated hazards & class of risk | Inherent Risk | WORK METHODS & CONTROL MEASURES Control measures to be adopted to eliminate or minimise assessed risks | Residual Risk | Responsibl e Person |
| --- | --- | --- | --- | --- | --- |

| PRINCIPAL CONTRACTOR | Principal Contractor for the Workplace | Energy Queensland / Ergon Energy (Project Specific) |  |
| --- | --- | --- | --- |
| WORKERS | Number of Workers who will carry out the activity. | 2 + |  |
| COMPETENCY | Qualifications / competencies required of persons carrying out work (licenses, qualifications, Permits) | General Safety Induction Card (Blue/White card) Statement of Attainment issued by a RTO or License or Certificate of Competency issued under previous State or Territory legislation High Risk Work Licence (if req’d) ESO |  |
| TRAINING | Details of training provided to employees carrying out the works | Austen Site Specific Induction Austen toolbox talks and daily pre-starts Energy Queensland / site inductions as required T0838 where required for live area access |  |
| SUPERVISION & MONITORING | Details of supervision & monitoring to be provided for this activity | Supervisor: | Supervisor: John Austen Leading Hand: Project Specific |
|  |  | Leading Hand: | N/A |
| PLANT & EQUIPMENT | What Plant and Equipment will be used to carry out this activity | Static Plant: Mobile Plant: | Plate compactor, Wacker Packer Excavator, Bobcat, Vacuum Excavation Truck, Trucks, Roller; |
|  |  | Hand Tools: | Fibreglass/Non Conductive Shovel(s), Insulated crow bar |
|  |  | Materials: | Marker Paint, Fill Materials |
| CHEMICALS | Will any Hazardous Materials and substances be used? | Diesel, Petrol, Oil |  |
| PPE | What Personal Protective Equipment is required for workers activity? | Refer Risk Analysis Page 1: Determination of appropriate equipment to use |  |
| SWMS REVIEW | Detail how the methods to be used to ensure that the SWMS used is kept up to date | Reviewed by John Austen during works and updated when conditions change. |  |
| ENVIRONMENTAL CONSIDERATIONS | Controls in place to protect the environment | Access available to Spill Kits onsite, erosion and sediment controls to be in place in accordance with EMP, dust suppression utilised as required, weed hygiene |  |
| LEGISLATION & CODES OF PRACTICE | Identify relevant Legislation, Standards and Codes of Practice relating to the work. | WH&S Act 2011, WH&S Reg 2011; Qld Electrical Safety Act 2002; Electrical Safety Regs 2013; Code of Practice:- Electrical Safety COP 2020-Working Near Overhead and Underground Electric Lines; Excavation Work 2021; Managing Risks of Plant 2021; Hazardous Manual Tasks 2021, Managing Noise and Preventing Hearing Loss at Work 2021; How to Manage Work Health and Safety Risks 2021; Work Health and Safety Consultation, Co-operation and Co-ordination 2021; Managing the Risks of Falls at Workplaces 2021; EPA Act 1994; EP Reg.2019; Biosecurity Act 2014 (Qld); Biosecurity Reg 2016 (Qld). |  |

“We, the undersigned, confirm this Safe Work Method Statement has been explained, its contents are clearly understood and we will comply with the stated requirements. We

also confirm that we have the required qualifications to undertake these activities.”

| Name | Signature | Date |
| --- | --- | --- |

“I confirm I have trained all the above workers in this SWMS and I hereby confirm that the documented precautions/controls & work methods will be complied with.”

Supervisor/Work Foreman/Leading Hand

| Name: | Position: | Date: | Signature: |
| --- | --- | --- | --- |
| John Austen | Site Supervisor |  |  |