|  | SAFE WORK METHOD STATEMENT (SWMS) MLCH-06 - VACUUM EXCAVATION |
| --- | --- |

This SWMS must be reviewed with all workers before work commences. Work must stop immediately if controls cannot be maintained or conditions change.

| Activity / Task | Vacuum Excavation / Non-Destructive Digging | Location | MILC - Millchester Substation / Project Specific |
| --- | --- | --- | --- |
| Scope | Applies to all Austen workers operating, assisting with, spotting, supervising or working near vacuum excavation activities. | SWMS No. | MLCH-06 |
| Training & Experience | Competent, trained and site inducted workers. Vacuum truck operators to be trained / verified. ESO required where working near live electrical services. | Prepared By | John Austen |
| Site Risk Assessment By | Site Supervisor: John Austen | Creation / Review Date | 15/05/2026 |
| Revision | A | Principal Contractor | Energy Queensland / Ergon Energy (Project Specific) |

PURPOSE

This SWMS sets out the hazards, risks and controls for vacuum excavation / non-destructive digging works. It is designed for civil, earthworks, utility and substation work environments where underground electrical, communications, gas, water, sewer, stormwater, earthing grids or other services may be present.

SCOPE

Vacuum excavation / hydro excavation / non-destructive digging.

Potholing and exposing underground services.

Working in substations, switchyards, road reserves and project sites.

Working near live underground electrical services and other underground assets.

Operation of vacuum excavation truck, pressure hose, suction hose, spoil tank and associated equipment.

Set up, operation, monitoring, clean up, spoil disposal and incident response.

CRITICAL RISKS AND MANDATORY CONTROLS

| Critical Risk | Possible Outcome | Mandatory Controls |
| --- | --- | --- |
| Underground service strike | Electric shock, fire, explosion, service outage or serious injury | Review DBYD / plans; locate services; pothole; use ESO where required; stop work if unidentified services are found. |
| Live underground electrical services | Electrocution, arc flash, burns or fatality | Treat all services as live until confirmed otherwise. Use insulated gloves and ESO where required. Maintain exclusion zones. |
| High pressure water jet | Injection injury, eye injury, laceration or service damage | Never point wand at people. Keep nozzle directed at ground. Do not bypass trigger. Use pressure suitable for the task and site requirements. |
| Vacuum suction hose | Crush, pinch, entanglement or struck-by injury | Maintain control of hose, avoid pinch points, keep workers clear of hose swing and never place body parts near suction opening. |
| Contaminated soil / asbestos / PCB / acid sulphate soil | Exposure, contamination, environmental harm | Assess before excavating. Stop work if suspected contamination is found. Use approved controls and disposal requirements. |
| Plant and pedestrian interaction | Crush injury or struck-by injury | Establish exclusion zones, use spotters, positive communication, reversing alarms and high visibility PPE. |
| Spoil / slurry management | Environmental harm, slip hazards, blocked drains | Contain spoil, prevent runoff, protect drains and dispose at approved location. |
| Noise and vibration | Hearing damage or fatigue | Use hearing protection, maintain equipment and manage exposure duration. |
| Hydraulic / mechanical failure | Injection injury, fire, equipment failure | Complete pre-starts, inspect hoses, report defects and remove unsafe equipment from service. |
| Working near traffic or public | Vehicle impact, public exposure | Traffic controls, barricades, signage and separation from work area. |

HAZARD IDENTIFICATION

| Hazard Group | Hazards Identified |
| --- | --- |
| Gravity | People falling, objects falling, slips/trips, falling into open excavations. |
| Kinetic | High pressure water jet, projectiles, pressurised releases, hose whip. |
| Mechanical | Caught between plant, struck by plant, pinch points, suction hose hazards. |
| Electrical | Live LV/HV services, electrocution, arc flash, induced voltage, step and touch potential. |
| Hazardous Substances | Contaminated soil, asbestos, PCB, acid sulphate soils, diesel, oils and hydraulic fluid. |
| Noise / Vibration | Hearing damage from vacuum equipment, plant noise and vibration exposure. |
| Muscular | Manual handling of hoses, bending, reaching, lifting, pushing and pulling. |
| Environmental | Spills, slurry runoff, sediment, dust, spoil disposal, flora/fauna impact. |
| Work Area | Traffic, public interface, restricted access, poor housekeeping and changing conditions. |

HIGH RISK WORK INTERFACE

Vacuum excavation may interface with high risk construction work including excavation, work near powered mobile plant, work near electrical installations/services, live substations, road/traffic interfaces, contaminated ground, and underground services. MLCH-02 Working Near Underground Services and MLCH-05 Excavations in a Live Substation must also be reviewed where applicable.

PPE REQUIREMENTS

| PPE Item | Requirement |
| --- | --- |
| Safety helmet | Required onsite and when working near plant, excavations or overhead hazards. |
| Safety footwear | Required at all times onsite. |
| Medium impact eye protection | Required as minimum. Face shield where water jet / splash risk is present. |
| Hi-vis long sleeve cotton clothing | Required for visibility and UV protection. |
| Task specific gloves | Durable waterproof / nitrile / rigger gloves as required. |
| Electrical / insulated gloves | 1000V rated gloves where required near live electrical services. |
| Hearing protection | Required when operating or working near vacuum excavation equipment. |
| Respiratory protection | Required where dust, fumes, silica or contaminated ground risk is present. |
| UV protection and 30+ sunscreen | Required for outdoor works. |

RISK RATING GUIDE

| Risk Rating | Required Action |
| --- | --- |
| Extreme | Do not proceed. Alternative method required. |
| High | Senior management / supervisor approval required before work proceeds. |
| Medium | Management responsibility must be specified and controls monitored. |
| Low | Work may proceed with normal supervision and routine controls. |
| Stop Work | All workers have authority to stop work if controls cannot be maintained. |

SEQUENCE OF WORK AND CONTROL MEASURES

| Sequence of Work | Hazards / Risk | Initial Risk | Work Methods & Control Measures | Residual Risk | Responsible Person |
| --- | --- | --- | --- | --- | --- |
| Planning, preparation and competency | Untrained workers; incorrect method; permits not in place | High | • All workers must hold current construction induction and complete the site induction. • Vacuum truck operator must be trained / competent / verified for the equipment. • Supervisor to confirm permits, service information, plant pre-starts and site requirements. • Review MLCH-02, MLCH-05 and MLCH-03 where underground services, excavation or live electrical assets are involved. • Confirm whether an Electrical Safety Observer (ESO) is required. • Confirm emergency response, first aid, communication methods and service damage response before work starts. | Low | Supervisor |
| Pre-start and consultation | Poor communication; changed conditions; unclear roles | Medium | • Attend Austen daily pre-start meeting before commencing work. • Discuss known services, potholing locations, pressure settings, plant movements, exclusion zones, spoil management and emergency response. • Confirm who is operating, spotting, supervising and acting as ESO where required. • Identify additional hazards and implement controls before work starts. • Stop work if the task changes or controls cannot be maintained. | Low | Supervisor / All Workers |
| Review service information | Inaccurate or incomplete underground service information | High | • Obtain and review DBYD / Before You Dig information and principal contractor service drawings. • Review site plans, as-built drawings, cable schedules and asset owner information. • Treat all services as live until positively identified and confirmed otherwise. • Do not rely on plans alone; verify services onsite through locating and potholing. • Confirm permit and excavation requirements before ground disturbance. | Low | Supervisor |
| Site setup and exclusion zones | Plant interaction; public exposure; unauthorised access | High | • Establish safe work area using barricades, cones, signage and exclusion zones. • Separate workers, pedestrians, public and traffic from vacuum truck and hoses. • Position vehicle on stable ground with safe access/egress. • Use traffic controls where work interfaces with roads or public access. • Maintain emergency access and clear escape routes. | Low | Supervisor / Operator |
| Plant and equipment pre-start | Faulty equipment; hose failure; mechanical failure | High | • Complete daily pre-start inspection before use. • Check vehicle, vacuum pump, water pump, pressure hose, suction hose, fittings, tank, emergency stops, lights, beacons, reversing alarm and fire extinguisher. • Inspect hoses and couplings for wear, damage, leaks or loose fittings. • Confirm spill kit and first aid equipment are available. • Remove defective equipment from service until repaired. | Low | Operator / Supervisor |
| Service locating and mark-up | Failure to locate underground services | High | • Use a competent locator where required. • Walk the work area and inspect pits, conduits, trenches, marker posts, valves and signs of services. • Mark known and suspected services using approved marking methods. • Maintain service markings during the works. • Stop work and reassess if service locations are unclear or inconsistent. | Low | Supervisor / Locator |
| Vacuum excavation near live electrical services | Electric shock; arc flash; cable damage | High | • ESO required where live underground electrical services are identified, suspected or required by site controls. • Use insulated gloves where required near live services. • Keep water jet directed at the ground and away from people, overhead assets and exposed live parts. • Do not expose or undermine live cables without suitable controls and supervision. • Stop work if unidentified cables, conduits, marker tape or unexpected ground conditions are found. | Low | Supervisor / ESO / Operator |
| Operating pressure hose | High-pressure injection injury; eye injury; service damage | High | • Only competent workers to operate pressure hose. • Never point pressure wand at people or body parts. • Never bypass or tie off the trigger. • Use pressure appropriate to the task, ground conditions and service risk. • Maintain firm footing and hose control. • Wear eye protection / face shield and gloves as required. | Low | Operator / All Workers |
| Operating suction hose | Crush, pinch, entanglement or suction injury | High | • Maintain control of suction hose at all times. • Keep hands, feet and loose clothing away from suction opening. • Avoid placing body parts between hose and fixed objects. • Maintain clear communication between hose operator and vacuum truck operator. • Stop work if hose becomes blocked, damaged or uncontrolled. | Low | Operator / All Workers |
| Excavating / potholing services | Service strike; conduit damage; collapse of hole edges | High | • Pothole carefully to expose services and confirm depth and location. • Do not use excessive force against services, conduits or cables. • Prevent undermining or unsupported exposure of services. • Protect exposed services with barriers, covers or supports as required. • Do not allow workers to enter unsupported excavations unless excavation controls are in place. | Low | Supervisor / Operator / All Workers |
| Working near gas, water, sewer and communications services | Explosion, fire, pressure release, flooding, comms outage or contamination | High | • Positively locate services before excavation. • Do not mechanically excavate under exposed services. • Obtain utility owner / principal contractor approval where required. • Protect exposed services from impact, bending, unsupported loading and vibration. • Notify principal contractor and utility owner immediately if damage occurs. | Low | Supervisor / Operator |
| Spoil, slurry and waste management | Environmental harm; slips; blocked drains; contamination | Medium | • Contain slurry and spoil within approved areas or tanks. • Prevent slurry entering drains, waterways or sensitive areas. • Manage spoil in accordance with project environmental requirements. • Contaminated spoil must be reported and disposed of using approved method. • Maintain housekeeping around the work area to prevent slips and trips. | Low | Supervisor / Operator |
| Contaminated ground or asbestos risk | Exposure to asbestos, PCB, acid sulphate soil or contaminants | High | • Review site asbestos register, contamination information and project environmental requirements. • Stop work if suspected asbestos conduit, contaminated soil, unusual odours, staining or unexpected material is found. • Do not break, cut, disturb or remove asbestos-containing material. • Isolate the area and notify supervisor / principal contractor. • Specialist controls and licensed contractors may be required before work continues. | Low | Supervisor / All Workers |
| Refuelling and fluid management | Fire, explosion, spill, skin/eye contact | High | • Refuel by competent person in a ventilated area away from ignition sources. • Turn plant off and allow hot surfaces to cool before refuelling. • Fire extinguisher and spill kit must be available. • Wear gloves and eye protection where required. • Clean and report spills immediately. | Low | Operator |
| Noise and manual handling | Hearing damage; muscle strain; fatigue | Medium | • Hearing protection required when operating or working near vacuum equipment. • Rotate tasks where practical. • Use team handling for heavy hoses or awkward positioning. • Avoid twisting, overreaching and prolonged awkward postures. • Take breaks and maintain hydration in hot conditions. | Low | All Workers |
| Unexpected service strike or damage | Electric shock, explosion, outage, flooding or environmental harm | High | • Stop work immediately if a service is contacted, damaged or unexpectedly exposed. • Move workers and plant clear where safe. • Do not touch exposed or damaged electrical services. • Notify John Austen / Site Supervisor and principal contractor immediately. • Contact Emergency Services or utility emergency contacts where required. • Preserve the scene and do not recommence until authorised and controls are reviewed. | Low | Supervisor / All Workers |
| Task observation and monitoring | Changed conditions; uncontrolled hazards; work outside SWMS scope | Medium | • Supervisor to monitor work activities and controls regularly. • All workers to monitor for additional hazards. • Review SWMS if conditions change, additional services are identified or work method changes. • Stop work if controls cannot be maintained. • Do not recommence until hazards are controlled and workers have been briefed. | Low | Supervisor / All Workers |
| Completion and clean up | Poor housekeeping; unsecured excavation; environmental harm | Medium | • Remove tools, rubbish, materials and trip hazards from work area. • Secure open holes, exposed services, barricades and signage until area is safe. • Dispose of spoil, slurry and contaminated waste in accordance with site requirements. • Wash down only in approved areas where runoff is controlled. • Complete permits, pre-start records, inspection records and close out documentation. | Low | Supervisor / All Workers |

ENVIRONMENTAL AND SITE CONTROLS

Spill kits must be available where plant, fuel, oil or chemicals are present.

Spoil and slurry must be contained and disposed of in accordance with site requirements.

Protect drains, waterways and sensitive areas from slurry, sediment, oil or contaminants.

Dust suppression must be used where required.

Contaminated soils, asbestos, PCB or acid sulphate soil risks must be reported and managed under specific controls.

Waste must be placed in correct bins or approved disposal areas.

Environmental incidents must be reported immediately to John Austen / Site Supervisor.

PROJECT INFORMATION AND REQUIREMENTS

| Principal Contractor | Energy Queensland / Ergon Energy (Project Specific) |
| --- | --- |
| Workers | 2+ or as required by task |
| Competency | General Safety Induction Card, site induction, task instruction, vacuum truck operator competency / VOC, service locating competency and ESO where required |
| Training | Austen Site Specific Induction, toolbox talks, daily pre-starts and Energy Queensland / site inductions as required |
| Supervision & Monitoring | John Austen / project supervisor to monitor work, inspect work areas and review controls |
| Plant & Equipment | Vacuum excavation truck, pressure hose, suction hose, water tank, spoil tank, service locator and project specific equipment |
| Tools and Equipment | Service plans, cable locator, non-conductive shovels, insulated tools, barricades, signage, radios, spill kits, fire extinguisher and first aid equipment |
| Chemicals | Diesel, petrol, oil, grease, hydraulic fluid or other substances associated with plant use |
| PPE | Refer to PPE section and site requirements |
| SWMS Review | Reviewed by John Austen during works and updated when conditions change |
| Legislation & Codes of Practice | WHS Act 2011; WHS Regulation 2011; Electrical Safety Act 2002; Electrical Safety Regulation 2013; Excavation Work Code of Practice 2021; Managing Risks of Plant in the Workplace 2021; Managing Electrical Risks in the Workplace 2021; Hazardous Manual Tasks Code of Practice 2021; How to Manage WHS Risks 2021; Environmental Protection Act 1994; Biosecurity Act 2014 |

EMERGENCY AND INCIDENT RESPONSE

Stop work immediately.

Make the area safe if it is safe to do so.

Keep workers and plant clear of damaged, exposed or pressurised services.

Do not touch any exposed or damaged electrical cable or conduit.

Notify John Austen / Site Supervisor and the principal contractor immediately.

Contact Emergency Services on 000 where required.

Contact electricity emergency on 131 962 where electrical assets may be involved.

Use spill kit and protect drains / waterways if safe to do so.

Preserve the incident scene where required.

Do not restart work until the hazard is controlled and the SWMS has been reviewed if required.

WORKER SIGN ON

We, the undersigned, confirm this Safe Work Method Statement has been explained, its contents are clearly understood and we will comply with the stated requirements. We also confirm that we have the required qualifications to undertake these activities.

| Name | Signature | Date |
| --- | --- | --- |

SUPERVISOR DECLARATION

I confirm I have trained all above workers in this SWMS and I hereby confirm that the documented precautions, controls and work methods will be complied with.

| Name | Position | Date | Signature |
| --- | --- | --- | --- |
| John Austen | Site Supervisor |  |  |

THINK SAFE - WORK SAFE - GO HOME SAFE